## Slide 1: Three Phase Motors
Topic 3: Testing Three Phase Motors

## Slide 2: Assumed prior learning
05_01_00
05_01_02
05_02_01
Notes: Note for navigation on site:
This information needs to be taken into account and needs to stated on the LMS, perhaps as part of the introduction?

## Slide 3: Outcomes
By the end of this unit the learner will:
List the necessary three phase motor electrical tests
Perform continuity tests on three phase motors
Perform insulation resistance tests on three phase motors
Complete a motor test form with the results of electrical tests

## Slide 4: Unit 2.2: Three Phase Motor Electrical Tests

## Slide 5: Introduction
Three phase induction motors, especially squirrel cage motors, are tough…really tough!
This is one of the reasons why they are so widely used and can be used in some pretty harsh environments like mines and factories.
Notes: Img01 = image of an induction motor in a real industrial setting e.g. https://encrypted-tbn0.gstatic.com/images?q=tbn:ANd9GcRUTKiDbgTaEgPU_xrZEqvsrHMZHHKtUoYzJbieDykYp3EiWepH

## Slide 6: Why test?
Faulty motors are unsafe and some faults can lead to injury or death.
Maintenance helps keep the motor running correctly and efficiently
There are moving and electrical parts which can wear out.
Motors are often moved and reinstalled which means lifting, handling and transporting.
But nothing is perfect so all three phase induction motors need to be regularly maintained and tested. Here’s why.
1
2
3
4
Notes: Reveal full point on clicking each number. Use a device to indicate to learners that they need to click number 1 to start with.

## Slide 7: Introduction
[Img2] You work in a food processing plant and receive a call that one of the motors which drives a conveyor belt is not working. Your job is to test this three phase motor and see if you can figure out what is wrong with it.
Notes: Replace with a cartoon strip or series of images with descriptions

## Slide 8: Safety first
When you work with motors you must put your safety and the safety of others first. You must complete the necessary Hazard Identification and Control (HIAC) Form.
Get help with HIAC Forms
Need help with HIACs? Click the button to go to Topic X in The World of an Electrician
Notes: Img02 = https://cdn.pixabay.com/photo/2014/04/02/10/38/sign-304093_960_720.png
Button 01 = direct learner to Topic X in Course 0

## Slide 9: Potential Hazards
Here are some of the potential hazards you should look out for:
Vehicles, traffic or mobile equipment
Hazardous Materials or Waste
Electricity, machinery, stored energy or machine isolation
Working at heights above 2m
Lifting and material handling
Work with Oxy-fuel gas mixtures
Notes: Present boxes with just a representative icon in each circle. On click/touch, reveal the full statement.
Display small animations to indicate that boxes can be clicked/touched

## Slide 10: What are the Potential Hazards?
You need to test a three phase AC motor.
It operates a 30m long conveyor belt
The motor is mounted on a bracket at one end of the conveyor belt.
Identify the hazards
Identify all the hazards that are present.
Notes: Img03 = image of a motor driving a conveyor belt in a food factory e.g. https://3l4sbp4ao2771ln0f54chhvm-wpengine.netdna-ssl.com/wp-content/uploads/2017/01/00-Interroll-application-example-for-food.jpg
Suppress global navigation – only way forward is Button 01
Button 01 = link to next slide
Focus on the image with additional text as support

## Slide 11: Potential Hazards
Which hazards apply to this situation? Drag them onto the picture.
Vehicles, traffic or mobile equipment
Hazardous Materials or Waste
Electricity, machinery, stored energy or machine isolation
Working at heights above 2m
Lifting and material handling
Work with Oxy-fuel gas mixtures
Img03
Check
Notes: Drag and drop activity.
Correct answer is “mobile equipment, electricity”
Button 01 = on click/touch check answers and provide feedback as follows:
Correct – Well done. You correctly identified all the potential hazards. Because you are working near a vehicle entrance there are very likely to be vehicles coming and going. The door is 2,5m high so you will be working at a height above 2m. There is definitely electricity, machinery and stored energy involved.
Incorrect – That is not quite right. Because you are working near a vehicle entrance there are very likely to be vehicles coming and going. The door is 2,5m high so you will be working at a height above 2m. There is definitely electricity, machinery and stored energy involved.

## Slide 12: Stop and Check?
Because there are some potential hazards associated with this job, you need to check that all the necessary safety controls related to these hazards are in place.
Learn about Safety Controls
If you are not sure what these safety controls are, you should stop this unit and refer back to Topic X in The World of an Electrician before continuing.
Notes: Img04 = https://upload.wikimedia.org/wikipedia/commons/9/9d/Stop_sign_light_red.svg
Button 01 = direct learner to Topic X in Course 0

## Slide 13: Before We Begin
Before you do any electrical tests, you must make sure that you have isolated and locked out the supply to the motor.
Learn about Isolating and Lock-Out Procedures
Make sure you know how to do this by referring to Topic X in The World of An Electrician.
Notes: Img05 = https://cdn.pixabay.com/photo/2016/07/01/22/38/industrial-safety-1492062_960_720.png
Button 01 = direct learner to Topic X in Course 0

## Slide 14: Be Prepared
Once you have
Identified all potential hazards
Made sure the necessary safety controls are in place
Isolated and locked out the motor, you can prepare to start your tests.
Check you multimeter
Open the terminal box
Remove the bridge pieces
1
2
3
Click on each box to learn more.
Notes: Present the following details on click/touch of each box. Present details in a popup window with a clear close button.
1 = Make sure your multimeter is working properly. If the batteries need replacing, replace them.
2 = See slide 15
3 = See slide 16

## Slide 15: Open the Terminal Box
You do not need to open up the motor to test it. You can access all the motor’s electrical components and terminals from inside the terminal box.
Look out for a wiring diagram on the inside of the terminal box cover showing how everything is connected to the terminal block
Img06
Img07
Notes: Img06 = photograph of someone unscrewing the terminal box with a screwdriver
Img07 = photograph of the inside of the terminal box with the terminal block labelled
Img08 = photograph of a terminal block diagram on the inside of a terminal box lid
Provide option to view all images full screen.

## Slide 16: Remove the Bridge Pieces
You might see some of the terminals connected or bridged with strips of metal. These allow you to control the direction of the motor.
Img09
Img10
If you see bridge pieces, disconnect them.
Notes: Img09 = photograph of a terminal block with a bridge piece
Img10 = photograph of someone unscrewing the terminal connections to remove the bridge piece
Provide option to view all image full screen.

## Slide 17: A Note on Wiring Diagrams
The names that different manufacturers give to each terminal may differ but U1, V1, W1, U2, V2 and W2 are quite common.
The wiring diagram gives details about how to wire the motor including where to place the bridge pieces in order to control its direction and how to wire it in star or delta configuration
Notes: Img08 = photograph of a terminal block diagram on the inside of a terminal box lid
Provide option to view all image full screen.

## Slide 18: Types of Electrical Tests
There are basically three types of electrical tests that you need to be able to do on three phase AC motors.
Continuity
Insulation resistance between conductors and earth
Click on each box to find out more.
Insulation resistance between conductors
Notes: Present the following details on click/touch of each box. Present details in a popup window with a clear close button.
Continuity – These test if there is a complete path through the stator phase windings for current to flow. We check that there are no breaks in the windings by measuring the ohmic resistance of the windings.
Insulation resistance between conductors and earth – These test that there are no short circuits between the windings and the motor frame.
Insulation resistance between conductors – These test that the insulation between the different windings in intact and that there are no short circuits between windings due to worn insulation.

## Slide 19: Continuity Tests
Now you are ready to start with the continuity tests.
Step 1
Step 2
Step 3
Step 4
Click each step to see what to do.
Notes: On click/touch of each step display the details for each step in a popup with a clear close button. As leaner moves through steps indicate which steps have been viewed by changing the button
See slide 19
See slide 20
See slide 21
See slide 22

## Slide 20: Step 1
Set your multimeter to the continuity setting which is often the same as the low Ω setting.
Img11
Notes: Img11 = photograph of a multimeter set to continuity clearly showing the setting symbol.

## Slide 21: Step 2
Draw the terminal block connections on a piece of paper if you do not have a printed diagram.
If there is a wiring diagram available label the terminals in your diagram like the wiring diagram.
Make sure that you have an electrical checklist to note down all your test results.
Img12
Img13
Notes: Img12 = photograph of a drawn terminal drawing alongside one that is printed
Img13 = image of a standard electrical check list
Provide option to view all image full screen.

## Slide 22: Step 3
Clip the black lead onto the top left terminal and test each of the other terminals to see which one shows continuity.
Your multimeter will show a resistance value and might beep.
Mark these two terminals and note the total resistance.
Img14
Img15
Notes: Img14 = photograph of black lead on terminal 1, red lead on another terminal and the multimeter showing a resistance reading
Img15 = photograph of the corresponding terminals marked with the measured resistance

## Slide 23: Step 4
Connect the black lead to the next terminal and repeat the process until you have connected the black lead to all of the terminals.
Mark which terminals are connected and what the resistance value is in each case.
Img16
Notes: Img16 = photograph of the black lead on terminal 3 and terminal 5 being tested with the red lead.

## Slide 24: Doing a Continuity Test
Watch the video to see how to do a continuity test and to learn what the readings mean.
Img17
Notes: Img17 = screenshot of Vid01 (see brief). Play video full screen

## Slide 25: Complete a Motor Test Form
Here is part of a typical motor test form.
Img18
See the test values
Click on the image to download the form or make your own.
Look at the test values.
Complete the Motor Test Form.
Indicate on the Motor test form if the readings are acceptable and if the windings are balanced.
Notes: Img18 = blank motor test form for the continuity tests section
Include option to view image full screen
Button 01 – link to contents of slide 26 as a popup

## Slide 26: Test Values
Post 1 – Post 2: none
Post 1 – Post 3: none
Post 1 – Post 4: none
Post 1 – Post 5: none
Post 1 – Post 6: 10.9Ω
Post 2 – Post 1: none
Post 2 – Post 3: none
Post 2 – Post 4: 10.7Ω
Post 2 – Post 5: none
Post 2 – Post 6: none
Post 3 – Post 1: none
Post 3 – Post 2: none
Post 3 – Post 4: none
Post 3 – Post 5: 10.7Ω
Post 3 – Post 6: none
Notes: Terminal labels and readings to be confirmed for an actual motor.

## Slide 27: Upload Your Motor Test Form
Take a picture of your completed form and upload it.
Choose image
Upload
Make sure you have labelled the block diagram indicating how the three windings are connected.
Notes: Img19 = https://cdn.pixabay.com/photo/2016/01/03/00/43/upload-1118929_960_720.png
Button 01 – Launch file selection window
Button 02 – Upload file

## Slide 28: Your Motor Test Form
Your completed form should have looked something like this.
The centrifugal switch has a resistance close to zero.
The start winding always has a resistance greater than the run winding.
Img20
Notes: Img20 = complete the form from slide 25 (img18) and reproduce the provided block diagram image with the correct diagram (see Img21 above) and values:
A1 – A2: 10.9Ω
B1 – B2: 10.7Ω
C1 – C2: 10.7Ω

## Slide 29: Insulation Resistance Tests
Electricity is very useful but only when it flows where we want it to!
Img22
Insulation resistance tests check if there is any breakdown in the insulation between a motor’s electrical components.
It is best to use an insulation resistance tester for these tests because of the high test voltages they produce.
1
2
Notes: Img22 = image of a insulation resistance tester e.g. https://www.instrumart.com/assets/1507-360.jpg

## Slide 30: Insulation Resistance Tests
We need to do two separate tests:
Watch how to do these insulation resistance tests
Test the insulation between the windings.
Test the insulation between each winding and the motor frame.
1
2
Ideally the resistance between the phase windings and the between the phase windings and the frame should be infinite.
Notes: Present boxes with just the number. On click/touch, reveal the full statement as a slide right animation
Display small animations to indicate that boxes can be clicked/touched
Button 01 = link to vid02. Play video full screen

## Slide 31: Complete the Motor Test Form
Download the motor test form or make your own. Complete the form with the results of the insulation resistance test results and indicate if all tests are within acceptable limits
Img23
See the test results
Download
Notes: Img23 = part of a blank motor test form
Include option to view image full screen
Button 01 = link to slide 32 as popup

## Slide 32
A1 – B1: ∞
A1 – C1: ∞
B1 – C1: ∞
A2 – B2: 3MΩ
A2 – C2: 0.83MΩ
B2 – C2: ∞
A1 – frame: ∞
A1 – frame: ∞
C1 – frame: ∞
A2 – frame: 0.1MΩ
B2 – frame: ∞
C2 – frame: ∞

## Slide 33: Upload Your Full Motor Test Form
Now take a picture of your completed form and upload it.
Choose image
Upload
Make sure that all the columns have been completed.
Notes: Img19 = https://cdn.pixabay.com/photo/2016/01/03/00/43/upload-1118929_960_720.png
Button 01 – Launch file selection window
Button 02 – Upload file

## Slide 34: Get Some Practice
Are you ready to do a full electrical test on a three phase motor?
Launch the simulator
Try this three phase motor test simulator.
Img24
Notes: Button 01 = link to motor test simulator (see brief)
If simulator is not possible, will need to develop questions.
Img24 = screenshot of simulator.

## Slide 35: Video Briefing – Vid01
Video of an electrician demonstrating how to do a continuity test. Pay special attention to
Safety procedures
Setting the multimeter to the correct setting and checking the shorted value
The process and sequence of connecting the leads
Seeing when the meter gives a reading and what this is
Connecting the terminals on the diagram and noting the resistance values
Analysing the resistance values and check the tolerances. Readings within 5% of each other indicate balanced windings
Repeat the test on a damaged motor and show readings obtained for
  Broken winding
  Unbalanced windings and what to do when this is the case
Demonstrate how to complete a motor test form with these results
Notes: See https://www.dropbox.com/s/fmte98gitax112u/3p%20motor%20test.mp4?dl=0
00:00 - 03:14 as a reference
Also see https://www.dropbox.com/s/c81f26n10t91c89/Testing%20Electrical%20motors.m4v?dl=0 as a reference

## Slide 36: Video Briefing – Vid02
Video of an electrician demonstrating how to test a do insulation resistance tests. Pay special attention to:
Why insulation may breakdown and what this causes (a burnout)
Use same winding configuration as discovered during continuity tests
The required insulation resistance tester setting selection (500V and Mohm)
Procedure to test insulation between phase windings and allowed readings (more than 1MΩ)
How to complete the motor test form
Make sure to include at least 1 test that fails and what to do (motor drying)
  Heaters
  Oven
  Low V DC
Procedure to test insulation between phase windings and motor frame and allowed readings (more than 0.5MΩ)
How to complete the motor test form
Make sure to include at least 1 test that fails
Notes: See https://www.dropbox.com/s/fmte98gitax112u/3p%20motor%20test.mp4?dl=0
03:015 - 06:42 as a reference
Also see https://www.dropbox.com/s/c81f26n10t91c89/Testing%20Electrical%20motors.m4v?dl=0 as a reference

## Slide 37: Motor Test Simulator