## Slide 1: Three Phase Motors
Topic 3: Connecting and Starting Three Phase Induction Motors

## Slide 2: Assumed prior learning
05_01_00
05_01_02
05_02_01
Notes: Note for navigation on site:
This information needs to be taken into account and needs to stated on the LMS, perhaps as part of the introduction?

## Slide 3: Outcomes
By the end of this unit the learner will:

## Slide 4: Unit 3.6: Manual and Semi-Automatics Start-Delta Starters

## Slide 5: Introduction
So far in this topic, we have created starters that work really well for smaller motors (4 horse power or less). But when big motors start up, they draw huge amounts of current; so much that they can affect other devices in the factory.
In this unit we will see how to solve this problem by reducing the amount of current large motors draw when starting.
Notes: Img01 = image of any large motor e.g. http://www.actom.co.za/wp-content/uploads/2016/10/Large-Motors-Duvha-Matla-Kriel-Oct-09-Small.jpg

## Slide 6: Why do big motors draw so much current?
Lets go back to the basics of induction motors to see why all this is a problem in the first place.
Img02
View the video to learn why induction motors draw more current when they start up.
Notes: Img02 = screenshot of Vid01 (see brief). Play video full screen

## Slide 7: What is the solution?
The solution lies in how we connect the coils of the motor together. We know one side of the coils must be connected to the three phase power (L1, L2 and L3). But there are 2 basic ways we can connect the other ends of the coils.
Click the buttons to see an overview of the possible motor winding connections.
Star Connections
Delta Connections
1
2
Notes: Button01 = on click open slide 8 as a popup
Button02 = on click open slide 9 as a popup

## Slide 8: Star connections
Star connections have the ends of the loads in all three phases connected together at a single point. Most often, a neutral line is also connected to this point in case the loads on each phase are not balanced. You will also see these connections called “Wye” or “Y” connections.
Y
Notes: Img03 = image of star connection – colour coded like this one and including the symbol “Y”

## Slide 9: Delta connections
Delta connections have the end of the load in one phase connected to the beginning of the load in the next phase. There is no neutral line.
They are called delta because they look like the Greek symbol for “d”.
Δ
Notes: Img04 = image of delta connection – colour coded like this one and including the symbol

## Slide 10: So what?
Watch the video to learn more.
You may be wondering what all this has to do with solving our initial problem. There is one more piece of the puzzle. Star and delta connections have some important effects on the voltage and current across and through the motor coils.
Vid05
Notes: Play vid05 full screen. See brief.

## Slide 11: A quick summary
Click on each box to find out more.
We have just seen that connecting loads, like the coils in a three phase motor, in star and delta configuration has important affects on the voltage across and current through these loads. Here is a short summary of what we have learnt.
Current in star connections
Voltage in star connections
1
2
Current in delta connections
3
Voltage in delta connections
4
Notes: Button01 = open slide 12 as a popup
Button02 = open slide 13 as a popup
Button03 = open slide 14 as a popup
Button04 = open slide 15 as a popup

## Slide 12: Current in a star connections
In a star connection, the current flowing through a line (the line current or IL) is equal to the current flowing through the connected coil (the phase current or IP).
This makes sense because there is only one path for the current to flow.
Line current
Phase current
IL = IP
Notes: Img07 = image like this one but make the IL and IP symbols bigger and remove the VP and VL symbols.

## Slide 13: Voltage in a star connections
In a star connection, the voltage drop between any two lines (the line voltage or VL) is equal to √3 (1.732) times the voltage across the connected coil (the phase voltage or VP).
Line voltage
Phase voltage
VL = √3 x VP
Notes: Img08 = image like this one but make the VL and VP symbols bigger and remove the IP and IL symbols.

## Slide 14: Current in a delta connections
In a delta connection, the current flowing through a line (the line current or IL) is equal to √3 (1.732) times the current flowing through the connected coil (the phase current or IP).
Line current
Phase current
IL = √3 x IP
Notes: Img09 = image like this one but make the IL and IP symbols bigger and remove the VP and VL symbols.

## Slide 15: Voltage in a star connections
In a delta connection, the voltage drop between any two lines (the line voltage or VL) is equal to the voltage drop across the connected coil (the phase voltage or VP).
Line voltage
Phase voltage
VL = VP
Notes: Img10 = image like this one but make the VL and VP symbols bigger and remove the IP and IL symbols.

## Slide 16: A quick summary
Star
Delta
Current
Voltage

## Slide 17: And the solution is…
In delta
In star
VP = VL
Maximum voltage available
Motor can produce maximum torque
Good for running
VP = VL/√3
Reduced voltage available
Motor cannot produce maximum torque
But motor draws much less current because of Ohm’s Law
If the voltage is less, the current must be less as R stays the same
Good for starting
Click each heading to see the solution to our original problem.
Notes: For each list on clicking heading reveal point 1 with a note to click again to reveal next point until all points revealed.

## Slide 18: How do you wire Star and Delta connections in motors?
Click on each connection type to see what the connection looks like in a three phase motor terminal block.
Img05
Img06
Notes: Img05 = see brief
Img06 = see brief

## Slide 19: Question 1
Drag the available bridge pieces onto the terminal to connect this motor up in star formation.
Submit
Notes: Drag and drop question:
See img10a for correct answer
Feedback:
Correct – Well done. You got it.
Incorrect – That is not correct. You need to connect L1 to A1, L2 to B1 and L3 to C1 for power. Then you need to connect A2 to B2 and B2 to C2 to make the star point. [Also show image of correct placement)
Button01= On click check answers and provide feedback

## Slide 20: Question 2
Drag the available bridge pieces onto the terminal to connect this motor up in delta formation.
Submit
Notes: Drag and drop question:
See img10b for correct answer
Feedback:
Correct – Well done. You got it.
Incorrect – That is not correct. You need to connect L1 to A1, L2 to B1 and L3 to C1 for power. Then you need to connect A2 to B2 and B2 to C2 to make the star point. [Also show image of correct placement)
Button01= On click check answers and provide feedback

## Slide 21: Question 3
Click on the circle that represents where you would take a reading of VL in the diagram.
1
3
A
2
Notes: Image hotspot question
Circle with A is correct answer.
Feedback:
Correct – Well done.
Incorrect
If choose 1: This is not correct. That is where you would measure line current (IL).
If choose 2: This is not correct. That is where you would measure phase voltage (VP).
If choose 3: This is not correct. That is where you would measure phase current (IP).

## Slide 22: Question 4
Click on the circle that represents where you would take a reading of IP in the diagram.
1
A
3
2
Notes: Image hotspot question
Circle with A is correct answer.
Feedback:
Correct – Well done.
Incorrect
If choose 1: This is not correct. That is where you would measure line current (IL).
If choose 2: This is not correct. That is where you would measure phase voltage (VP).
If choose 3: This is not correct. That is where you would measure line voltage (VL).

## Slide 23: Question 5
A 380 volt supply is connected to a three phase, 380 volt induction motor. What voltage would be measured across each phase if the motor was connected in:
Star
Delta
Submit
V
V
Notes: Cloze question:
Star – between 219 and 220 V
Delta – 380V
Feedback:
Star:
Correct – Well done. You got it. In star the VP = VL/√3 = 380V/1.732 = 219.4V.
Incorrect – That is not correct. Remember, in star the VP = VL/√3 = 380V/1.732 = 219.4V.
Delta:
Correct – Well done. You got it. In delta the VP = VL = 380V.
Incorrect – That is not correct. Remember, in delta the VP = VL = 380V.
Button01= On click check answers and provide feedback

## Slide 24: Question 6
Complete the table, correct to 0 decimal places.
Submit
Connection | IL | IP | VL | VP
Star | 25 | 25 | 779 | 450
Delta | 69 | 40 | 600 | 600
Delta | 20 | 12 | 210 | 210
Star | 18 | 18 | 320 | 185
Notes: Cloze question:
Answers in table in orange
Feedback:
Present the table with correct answers in GREEN and incorrect answers in RED with the correct answers in GREEN in brackets.
Also display a link to the summary on slide 16.
Button01= On click check answers and provide feedback

## Slide 25: Safety first
When you work with motors you must put your safety and the safety of others first. You must complete the necessary Hazard Identification and Control (HIAC) Form.
Get help with HIAC Forms
Need help with HIACs? Click the button to go to Topic X in The World of an Electrician
Notes: Img11 = https://cdn.pixabay.com/photo/2014/04/02/10/38/sign-304093_960_720.png
Button 01 = direct learner to Topic X in Course 0

## Slide 26: Before We Begin
Before you do any work on a motor, you must make sure that you have isolated and locked out the supply to the motor.
Learn about Isolating and Lock-Out Procedures
Make sure you know how to do this by referring to Topic X in The World of An Electrician.
Notes: Img12 =
Button 01 = direct learner to Topic X in Course 0

## Slide 27: The Star-Delta Starter
Obviously, manually swopping the connections in the motor terminal from star to delta after the motor starts would be a silly (and dangerous) idea.
This is why we use 2 contactors – on wired in star and the other in delta – and switch between them.
Notes: Img15 = image of the a simplified star-delta starter main circuit like this one (https://i.pinimg.com/originals/10/81/75/108175882c7cdc67c4a2fc76779b3f24.png).

## Slide 28: Review the basic DOL starter
Click on the images to remind yourself what the DOL main and control circuits look like.
Before we go further, lets review the basic main and control circuits for the Direct Online starter.
Img13
Img14
Notes: Img13 = Img09 from 07_03_01
Img14 = Img15 (5 of 5) from 07_03_01

## Slide 29: How do you wire the main circuit?
Watch the video to see how to wire up the main circuit for the start-delta starter.
The key parts of the main circuit are the 2 contactors wired in star and delta.
Img15
Notes: Img15 = screenshot of Vid02 (see brief)

## Slide 30: The main circuit diagram?
Click on the image to see the main circuit full screen.
Before, we move on, have another look at the main circuit diagram for the star-delta starter.
Img15a
Notes: Img15a = see brief

## Slide 31: Wire it up
Practice wiring the main star-delta starter circuit using the motor wiring simulator
Click on the image to access the motor wiring simulator.
Img16
Notes: Img16 = screenshot of Int01 (see brief)

## Slide 32: Upload your control circuit diagram
Draw your own version of the main star-delta starter circuit. Take a photo of your completed circuit and upload it to your online portfolio.
Choose image
Upload
Notes: Img17 = https://cdn.pixabay.com/photo/2016/01/03/00/43/upload-1118929_960_720.png
Button 01 – Launch file selection window
Button 02 – Upload file

## Slide 33: The control circuit?
As we saw from the main circuit, we need to find a way to switch between the start (star) and run (delta) contactors after a few seconds of the motor starting.
There are a few way we can do this.
Manually with a lever system
Semi-automatically with a push button system
1
2
Automatically with a timer system
3
Click each box to find out more.
Notes: Button01 = on click display the following as a popup – “This is an old method that is not used much nowadays. It involves a special mechanical contraption with a lever that one physically pushes from the start to run position.”
Button02 = on click display the following as a popup – “This is a more modern method that is sometimes still used. It involves a single start button which when pressed and held in activates the start (star) contactor and when released, switched the motor over to the run (delta) contactor.”
Button03 = on click display the following as a popup – “In this method, a timer is used to automatically switch over from the start (star) to the run (delta) contactor after a pre-determined time. Often, all the contactors and control components are integrated into a single physical device. This is how most start-delta starters today work.”

## Slide 34: How do you wire a manual star-delta starter?
Even though manual starters are seldom used anymore, they still give has a great sense of how the basic control system works.
Watch the video showing how to wire a manual star-delta starter and how it works.
Img18
Notes: Img18 = screenshot of Vid03 (see brief). Play video full screen.

## Slide 35: The manual star-delta starter
Manual star-delta starters are purely mechanical devices. Even though they are old they are still pretty ingenious.
Click on the button to play with a manual starter simulation.
Open the manual star-delta starter simulation
Notes: Img18a = photo of the inside of a manual star-delta starter (e.g. https://i.ytimg.com/vi/dqSw4rifhGE/maxresdefault.jpg)
Button01 = on click present Int02 (see brief) full screen.

## Slide 36: Upload your control circuit diagram
Draw your own version of the manual star-delta starter control circuit. Take a photo of your completed circuit and upload it to your online portfolio.
Choose image
Upload
Notes: Img19 = https://cdn.pixabay.com/photo/2016/01/03/00/43/upload-1118929_960_720.png
Button 01 – Launch file selection window
Button 02 – Upload file

## Slide 37: The semi-automatic star-delta starter
In the semi-automatic starter there is a start and stop button. You hold the start button in for start and then let it go to switch to run.
Watch the video to see a semi-automatic star-delta starter in action and how it is connected.
Img20
Notes: Img20 = screenshot of Vid04 (see brief). Play video full screen.

## Slide 38: The semi-automatic star-delta starter
The semi-automatic star-delta starter is a very clever control circuit.
Click on the image to a larger version of the semi-automatic star-delta starter control circuit.
Notes: Img21 = diagram of semi-automatic star-delta starter (see brief).

## Slide 39: Wire it up
Practice wiring the semi-automatic star-delta starter control circuit using the motor wiring simulator
Click on the image to access the motor wiring simulator.
Img22
Notes: Img22 = screenshot of Int03 (see brief)

## Slide 40: Upload your control circuit diagram
Draw your own version of the semi-automatic star-delta starter control circuit. Take a photo of your completed circuit and upload it to your online portfolio.
Choose image
Upload
Notes: Img23 = https://cdn.pixabay.com/photo/2016/01/03/00/43/upload-1118929_960_720.png
Button 01 – Launch file selection window
Button 02 – Upload file

## Slide 41: Video Briefing – Vid01
Animated video explaining why induction motor draw more current and cause a voltage drop on the line when starting. Explain the following:
Current in the coils of the stator creates a rotating magnetic field.
This rotating magnetic field cuts the bars of the rotor and induces a current in these bars (electromagnetic induction)
This induced current creates a magnetic field in the rotator which tries to align with the stator rotating magnetic field causing the rotor to spin.
Remember that the greater the rate of change of the magnetic field cutting a conductor, the greater the current induced
At start-up, the rate of change of the stator field cutting the rotor bars is very high because the difference in the speed of the stator rotating field and the rotor is very big. Therefore the current induced in the rotor bars is very high.
But, the current in the stator coils and rotor bars is linked by transformer action, so there must be a high current flowing in the stator coils as well.
The bigger the motor, the bigger these current flows are and the bigger the problem we have.
Notes: See https://v637g.app.goo.gl/v7kAfwvL3RNkXPMU6 as a reference. If necessary, this video clip could be provided to learners instead.

## Slide 42: Image Briefing – Img05 (1 of 4)
On click of the image rotate through the following images:
This is the schematic representation of the Star connection.
Notes: Colour code windings like image03 and img04

## Slide 43: Image Briefing – Img05 (2 of 4)
We can connect either the A1, B1, C1 or A2, B2, C2 ends of the windings together. The other ends of the wings are connected to the three phase power
Notes: Colour code windings like image03 and img04

## Slide 44: Image Briefing – Img05 (3 of 4)
This is what the Star connection looks like in the motor terminal box. We use jumpers to connect the ends of the windings together. Note that the windings are also often called U, V and W as in this picture
Notes: Photo of a star connection in motor terminal box.

## Slide 45: Image Briefing – Img05 (4 of 4)
You may see Star connected motors represented with this symbol.
Motor
Three phase AC
Star connection

## Slide 46: Image Briefing – Img06 (1 of 4)
On click of the image rotate through the following images:
This is the schematic representation of the Delta connection.
Notes: Colour code windings like image03 and img04

## Slide 47: Image Briefing – Img06 (2 of 4)
We can connect either the A1 to B2, B1 to C2 and C1 to A2 or C1 to B2, B1 to A2 and A1 to C2. We can also connect power to A1, B1 and C1 or A2, B2 and C2.
Notes: Colour code windings like image03 and img04

## Slide 48: Image Briefing – Img06 (3 of 4)
This is what the Delta connection looks like in the motor terminal box. We use jumpers to connect the ends of the windings together. Note that the windings are also often called U, V and W as in this picture.
Notes: Photo of a delta connection in motor terminal box.

## Slide 49: Image Briefing – Img06 (4 of 4)
You may see Delta connected motors represented with this symbol.
Motor
Three phase AC
Delta connection
Notes: Photo of a star connection in motor terminal box.

## Slide 50: Video Briefing – Vid02 (1 of 2)
Demonstration video presented by an expert electrician showing and explaining the wiring of the main star-delta circuit (wire according to the diagram on 2 of 2).
Wire up the motor control circuit breaker and the Overload relay – explain that we are placing the OL on the line side of the main/delta junction, and what this means (we have to set the overload to the full motor current rating)
Wire in the main contactor between protection and motor and connect motor - U1 – L1, V1 – L2, W1 – L3
Wire up the delta contactor and connect it to the motor and to L1, L2, L3 so that W2 – U1 – L1, U2 – V1 – L1, V2 – W1 – L3
Wire up the star contactor and connect it to the motor or to the leads running to the delta contactor U2 – U2, V2 – V2, W2 – W2
At each step above draw in that part of the circuit until the whole main circuit diagram is complete.

## Slide 51: Video Briefing – Vid02 (2 of 2)

## Slide 52: Image Briefing – Img15a (1 of 2)
Reproduce this image with 2 buttons that highlight the star and delta parts when clicked.
Star this slide
Delta next slide
Star
Delta

## Slide 53: Image Briefing – Img15a (2 of 2)
Star
Delta

## Slide 54: Interactive Briefing – Int01 (1 of 4)
Instructions
To add a wire between 2 points, click the starting connection and then click the ending connection.
To delete a wire, click on it and then click the Delete icon in the top right corner.
To change the colour of a wire, click on it and then click on the colour.
To move a component, click and drag it to a new position.
Practice
Connect the motor protection breaker circuit breaker up to the contactor
Test
Forward
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
MPCB
L1
L2
L3
T1
T2
T3
Notes: White circles on components are wire connection points
Make wires curve around components
When connected components are moved, have wires stay connected
On click of first connection, highlight connection point and start to draw wire and have end of wire follow finger/mouse until next connection. Use 2 second time delay on second connection before making the connection. When second connection is selected, highlight it also.

## Slide 55: Interactive Briefing – Int01 (2 of 4)
Test
Instructions
Print
R
W
B
Wire up the 3P Star-Delta main circuit.
See diagram
ContactorM
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
MPCB
L1
L2
L3
T1
T2
T3
Overload Relay
L1
L2
L3
T1
T2
T3
NO
NO
NC
NC
3M
U1
V1
W1
E
U2
V2
W2
ContactorD
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
ContactorS
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
Notes: Fix position of power
Fix position of motor and terminals
Present other components unconnected and unpositioned.
Button01 = on click test circuit connections. Highlight all connections that are incorrect. See next slide for all correct connections
Button02 = display the instructions on previous slide in a pop-up window.
Button03 = print a jpg or pdf version of the final circuit for the learner to download and save.
Button04 = display the control circuit diagram as (3 of 4 – same as Img15)

## Slide 56: Interactive Briefing – Int01 (3 of 4)

## Slide 57: Interactive Briefing – Int01 (4 of 4)
Test
Instructions
Print
R
W
B
Wire up the 3P Star-Delta main circuit.
See diagram
ContactorM
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
MPCB
L1
L2
L3
T1
T2
T3
Overload Relay
L1
L2
L3
T1
T2
T3
NO
NO
NC
NC
3M
U1
V1
W1
E
U2
V2
W2
ContactorD
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
ContactorS
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
Notes: Fix position of power
Fix position of motor and terminals
Present other components unconnected and unpositioned.
Button01 = on click test circuit connections. Highlight all connections that are incorrect. See next slide for all correct connections
Button02 = display the instructions on previous slide in a pop-up window.
Button03 = print a jpg or pdf version of the final circuit for the learner to download and save.
Button04 = display the control circuit diagram as (3 of 4 – same as Img15)

## Slide 58: Video Briefing – Vid03
Demonstration video presented by an expert electrician showing and explaining the wiring of the manual star-delta starter.
Show how the starter works – push the leaver and see how the contacts move
Demonstrate how to wire the starter
Work through the control circuit explaining how it shifts from one contactor to the other.

## Slide 59: Interactive Briefing – Int02 (1 of 3)
Create an interactive manual star-delta starter.
START
RUN
Notes: Switch has 3 positions – off, start, run. Image currently in “off” position
Start engages Star circuit (Blue contacts closed – only for briefing – don’t mark as blue) – highlight conducting conductors and the fact that the following connections are made: A1 – A2, B1 – B2, C1 – C2 and A2 - B2 – C2 (see 2 of 3)
Run engages Delta circuit (RED contacts closed – only for briefing – don’t mark as blue) – highlight conducting conductors and the fact that the following connections are made: A1 – C2, B1 – A2, C1 – B2 (see 3 of 3)

## Slide 60: Interactive Briefing – Int02 (2 of 3)

## Slide 61: Interactive Briefing – Int02 (3 of 3)

## Slide 62: Video Briefing – Vid04
Demonstration video presented by an expert electrician showing and explaining the control circuit and wiring of the semi-automatic star-delta starter.
Show how the starter works – push the start button in for star and then release for delta
Show the control circuit diagram and explain, step-by-step how the starter works
  Motor stopped
  Start button pressed and held
    Star coil energizes
    S1 closes
    Main coil energizes
    M1 closes
    S2 opens
    Motor is running in star
  Start button released
    Star coil de-energizes
    S1 opens but Main coil retained by M1
    S2 closes
    Delta coil energizes
    D1 opens to prevent Star coil form energizing (interlock)
    Motor running in delta
  Stop button pressed
    Mail and Delta coils de-energize
    M1 opens
    D1 closes
Show how the control circuit is wired in reality.

## Slide 63: Image Briefing – Img21
Recreate the diagram in the same way as all other diagrams in this topic have been drawn i.e. use all the same symbols.

## Slide 64: Interactive Briefing – Int03 (1 of 3)
Instructions
To add a wire between 2 points, click the starting connection and then click the ending connection.
To delete a wire, click on it and then click the Delete icon in the top right corner.
To change the colour of a wire, click on it and then click on the colour.
To move a component, click and drag it to a new position.
Practice
Connect the motor protection breaker circuit breaker up to the contactor
Test
Forward
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
MPCB
L1
L2
L3
T1
T2
T3
Notes: White circles on components are wire connection points
Make wires curve around components
When connected components are moved, have wires stay connected
On click of first connection, highlight connection point and start to draw wire and have end of wire follow finger/mouse until next connection. Use 2 second time delay on second connection before making the connection. When second connection is selected, highlight it also.

## Slide 65: Interactive Briefing – Int03 (2 of 3)
Test
Instructions
Print
R
W
B
Wire up the semi-automatic SD starter as per the diagram
See diagram
ContactorM
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
Overload Relay
L1
L2
L3
T1
T2
T3
NO
NO
NC
NC
ContactorD
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
ContactorS
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
Breaker1
L1
T1
Breaker2
L1
T1
Stop
Start
Notes: Fix position of power
Fix position of motor and terminals
Present other components unconnected and unpositioned.
Button01 = on click test circuit connections. Highlight all connections that are incorrect. See next slide for all correct connections
Button02 = display the instructions on previous slide in a pop-up window.
Button03 = print a jpg or pdf version of the final circuit for the learner to download and save.
Button04 = display the control circuit diagram (img21)

## Slide 66: Interactive Briefing – Int03 (2 of 3)
Test
Instructions
Print
R
W
B
Wire up the semi-automatic SD starter as per the diagram
See diagram
ContactorM
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
Overload Relay
L1
L2
L3
T1
T2
T3
NO
NO
NC
NC
ContactorD
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
ContactorS
L1
L2
L3
T1
T2
T3
A1
A2
NO
NO
NC
NC
Start
Breaker1
L1
T1
Breaker2
L1
T1
Stop

## Slide 67: Video Briefing – Vid05 (1 of 5)
Screencast video with a professional electrician r explaining how star and delta connections affect phase current and voltage.
Start with a quick recap of three phase electricity.
Single phase needs 2 wires – three phase needs 3 or 4 - therefore much more efficient – explain as in https://www.youtube.com/watch?v=quABfe4Ev3s up to 2:28

## Slide 68: Video Briefing – Vid05 (2 of 5)
Line current
Phase current
IL = IP
Explain the difference between the line current and the phase current in the star connection.
Explain why line current = phase current – show that there is only 1 path for the current to flow from the line to the phase.
Therefore if there are 20A flowing through the line, 20A will be flowing through the phase and the load.
Explain why the star point is not a short circuit – if loads are balanced, current at this point is zero (explain this by looking at the three phase sine waves and visually inferring the total current at any instant. In this image the max current is 1A but it could be any amount in a balanced system – where the same amount of current is being drawn by each load.

## Slide 69: Video Briefing – Vid05 (3 of 5)
Explain the difference between the line and phase voltage in the star connection.
Explain why line voltage is phase voltage x sqrt3 – in a 220V system, we know that the voltage drop across any one phase is 220V. But the voltage drop between 2 different phases (i.e. line voltage) is greater (refer to the three phase sine waves e.g. between phase 1 and 2 and any instant). Without going into all the Maths, it turns out that this difference is always sqrt3 more than the phase voltage of any phase.
So line voltage = phase voltage x sqrt3
If phase voltage is 220V, line voltage will be 220 x sqrt3 = about 380V.
If line voltage is 380V, phase voltage = 380V/sqrt3 = about 220V. This is why the single phase power in your house is 220V.
Line voltage
Phase voltage
VL = √3 x VP

## Slide 70: Video Briefing – Vid05 (4 of 5)
Now let’s look at delta connections. The bottom line is the relationships between phase and line currents and voltages are the reverse of star connections.
Explain the difference between the line current and the phase current in the delta connection.
Explain why line current = phase current x sqrt3 – show that there are now 2 paths for the current to flow so it splits. Again without going into the maths, it turns out that the line current = phase current x sqrt3.
If the phase current is 20A, this means the line current at any instant will be 20 x sqrt3 = about 34A.
Line current
Phase current
IL = √3 x IP

## Slide 71: Video Briefing – Vid05 (5 of 5)
Explain the difference between the line and phase voltage in the delta connection.
We can clearly see that the voltage drop across any of the loads will be the same as the voltage drop between the 2 corresponding lines because they form a parallel circuit and the voltage drop across parallel circuits are always the same.
Line voltage
Phase voltage
VL = VP